## 2019-2020
|  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799 | [7 empty] | INFRASTRUCTURE SERVICES DEPARTMENT | [9 empty] | 91 Adelaide Street BLAYNEY NSW 2799
|  | Blayney Sewage Treatment Works - Licence Point Sampling | [18 empty] | Blayney Sewage Treatment Works - Licence Point Sampling
|  | License Point No. |  |  |  | 1 |  |  | Point 1 to be sampled if discharge to river occurs | [11 empty] | License Point No. |  |  | 3
|  | Period |  |  |  | 2019-2020 | [14 empty] | Period |  |  | 2019-2020
|  | Sampling Frequency |  |  |  | If discharge to creek occurs | [14 empty] | Sampling Frequency |  |  | Monthly
|  | Published Date | [18 empty] | Published Date
Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm | Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L)
|  | Point 1 License Conditions 100%ile | [18 empty] | Approved Concentration Limit
|  | 30 |  | 30 |  | 6.5-8.5 | 600 |  | 10 |  | 15 |  | 1 | N/A | 2 | [5 empty] | No limit or range defined in licence
2020-01-07 | 2020-01-21 | < | 5 |  | 27 | 7.4 |  | 3800 | < | 5 |  | 3.2 | 0.25 | 0.35 | < | 0.5 |  |  | 2019-04-10 | 2019-04-23 | 5 |  | 7 | 8.64 |  | 40 | < | 5 |  | 1.7 | 0.41 |  | < | 0.5
2020-02-12 | 2020-02-25 | < | 5 |  | 1 | 7.2 |  | 42 | < | 5 |  | 6.2 | 0.38 | 0.2 | < | 0.5 |  |  | 2019-05-08 | 2019-05-22 | 8 |  | 2 | 7.84 | < | 1 | < | 5 |  | 7.8 | 0.26 |  |  | 2.8
2020-03-11 | 2020-03-24 | < | 5 |  | 2 | 7.34 |  | 100 | < | 5 |  | 5.7 | 0.57 | 0.23 | < | 0.5 | 50 | 56 | 2019-06-04 | 2019-06-19 | 9 |  | 3 | 7.66 |  | 15 | < | 5 |  | 8.8 | 0.69 |  |  | 3.2
[19 empty] | 2019-07-09 | 2019-07-22 | 6 |  | 4 | 7.72 |  | 4 | < | 5 |  | 7.1 | 0.2 |  |  | 2.1
[19 empty] | 2019-08-14 | 2019-08-27 | 5 |  | 11 | 9.64 | < | 1 | < | 5 |  | 9.1 | 0.2 |  | < | 0.5
[19 empty] | 2019-09-19 | 2019-10-01 | 5 |  | 6 | 8.75 |  | 15 | < | 5 |  | 3.2 | 0.23 |  | < | 0.5
[19 empty] | 2019-10-17 | 2019-10-30 | 5 |  | 5 | 8.89 |  | 6 | < | 5 |  | 6.3 | 0.26 |  | < | 0.5
[19 empty] | 2019-11-19 | 2019-12-05 | 6 |  | 7 | 8.24 |  | 47 | < | 5 |  | 7 | 0.21 |  | < | 0.5
[19 empty] | 2019-12-11 | 2019-12-23 | 5 |  | 6 | 7.76 |  | 14 | < | 5 |  | 5.2 | 0.66 |  | < | 0.5
CVO Effluent transfer System Suspended 11/12/2019
No of Samples Collected |  | 3 |  | 3 | 3 | 3 | 3 |  | 3 |  | 3 |  | 3 | 3 | 3 |  |  |  | No of Samples Collected |  | 9 | 9 | 9 | 9 | 9 |  | 9 |  | 9 |  | 9 | 0 | 9
Lowest Sample Value |  | < | 5 |  | 1 | 7.2 | 42 |  | < | 5 | < | 3.2 | 0.25 | 0.2 | < | 0.5 |  |  | Lowest Sample Value |  | 5 |  | 2 | 7.66 | 1 |  | < | 5 | < | 1.7 | 0.2 | 0 | < | 0.5
Mean of Samples |  | 5 | 1.6667 | 10 |  | 7.3133 | 1314 |  | 5 | 1.6667 | 5.0333 |  | 0.4 | 0.26 | 0.5 |  |  |  | Mean of Samples |  | 6 | 5.6667 |  | 8.3489 | 15.8889 |  | 5 | 5 | 6.2444 |  | 0.34667 | #DIV/0! | 1.2333
Highest Sample Value |  | 5 |  | 27 |  | 7.4 | 3800 |  | 5 |  | 6.2 |  | 0.57 | 0.35 | 0.5 |  |  |  | Highest Sample Value |  | 9 | 11 |  | 9.64 | 47 |  | 5 |  | 9.1 |  | 0.69 | 0 | 3.2
37095000
|  | 185.475 |  | 370.95 |  | 271.2881 | 48742.83 |  | 185.475 |  | 186.7115 |  | 14.838 | 9.6447
|  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799
Blayney Sewage Treatment Works - Licence Point Sampling
|  | License Point No. |  |  |  | 2
|  | Period |  |  |  | 2019-2020
|  | Sampling Frequency |  |  |  | Yearly
Published Date
Date Sample Taken | Date Reported | Biological Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm |  | Catch Pond
|  | Approved Concentration Limit | [16 empty] | Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm
|  | No limit or range defined in licence | [18 empty] | Catch Pond Summary
2019-07-09 | 2019-07-22 | < | 5 |  | 4 | 7.76 |  | 2 | < | 5 |  | 8.6 | 0.21 | 0.2 |  | 3.4 |  |  | 2019-08-14 | 2019-08-28 | 5 |  | 7 | 7.24 |  | 6700 | < | 5 |  | 9.6 | 0.19 |  | 0.7
2019-08-14 | 2019-08-27 | < | 5 |  | 12 | 9.75 |  | 1 | < | 5 |  | 7.8 | 0.17 | 0.2 |  | 0.7 |  |  | 2019-09-19 | 2019-10-01 | 5 |  | 6 | 7.28 |  | 1300 | < | 5 |  | 7.7 | 0.15 |  | 1
2019-09-19 | 2019-10-01 |  | 9 |  | 12 | 8.7 |  | 5 | < | 5 |  | 3.5 | 0.3 | 0.55 | < | 0.5 |  |  | 2019-10-17 | 2019-10-30 | 5 |  | 5 | 7.2 |  | 1400 | < | 5 |  | 9.5 | 0.24 |  | 2.1 | 64 | 68
2019-10-17 | 2019-10-30 |  | 5 |  | 5 | 8.85 |  | 510 | < | 5 |  | 6.5 | 0.25 | 0.32 | < | 0.5 |  |  | 2020-03-11 | 2020-03-24 | 5 |  | 4 | 7.4 |  | 2800 | < | 5 |  | 8.7 | 0.56 |  | 1.3 | 69 | 73
2019-12-11 | 2019-12-23 | < | 5 |  | 6 | 8.05 |  | 28 | < | 5 |  | 4.4 | 0.86 | 0.26 | < | 0.5 |  |  | 2020-04-15 | 2020-04-29 | 5 |  | 4 | 7.24 |  | 1100 | < | 5 |  | 6.6 | 0.44 |  | 1.4 | 70 | 74
2020-01-07 | 2020-01-21 | < | 5 |  | 12 | 8.72 |  | 160 | < | 5 |  | 3.7 | 0.26 | 0.22 | < | 0.5
2020-02-12 | 2020-02-25 | < | 5 |  | 1 | 7.84 |  | 120 | < | 5 |  | 6.9 | 0.37 | 0.3 | < | 0.5
2020-03-11 | 2020-03-24 | < | 5 |  | 9 | 7.74 |  | 75 | < | 5 |  | 7.3 | 0.63 | 0.56 | < | 0.5 | 65 | 69
No of Samples Collected |  | 8 |  | 8 | 8 | 8 | 8 |  | 8 |  | 8 |  | 8 | 8 | 8 |  | 1 | 1 | No of Samples Collected |  | 5 | 5 | 5 | 5 | 5 |  | 5 |  | 5 |  | 5 | 5 |  | 3 | 3
Lowest Sample Value |  | < | 5 |  | 1 | 7.74 | 1 |  | < | 5 | < | 3.5 | 0.17 | 0.2 | < | 0.5 | 65 | 69 | Lowest Sample Value |  | 5 |  | 4 | 7.2 | 1100 |  |  | 5 |  | 6.6 | 0.15 |  | 0.7 | 64 | 68
Mean of Samples |  | 5.5 | 4.8889 | 7.625 |  | 8.4262 | 112.625 |  | 5 | 4.4444 | 6.0875 |  | 0.38125 | 0.32625 | 0.8875 |  | 65 | 69 | Mean of Samples |  | 5 | 5.2 |  | 7.272 | 2660 |  | 5 | 2.7778 | 8.42 |  | 0.316 | 1.3 |  | 67.6667 | 71.6667
Highest Sample Value |  | 9 |  | 12 |  | 9.75 | 510 |  | 5 |  | 8.6 |  | 0.86 | 0.56 | 3.4 |  | 65 | 69 | Highest Sample Value |  | 5 | 7 |  | 7.4 | 6700 |  | 5 |  | 9.6 |  | 0.56 | 2.1 |  | 70 | 74

## 2020-2021
|  |  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799 | [7 empty] | INFRASTRUCTURE SERVICES DEPARTMENT | [9 empty] | 91 Adelaide Street BLAYNEY NSW 2799
|  |  | Blayney Sewage Treatment Works - Licence Point Sampling | [18 empty] | Blayney Sewage Treatment Works - Licence Point Sampling
|  |  | License Point No. |  |  |  | 1 | [14 empty] | License Point No. |  |  | 3
|  |  | Period |  |  |  | 2021 - 2022 | [14 empty] | Period |  |  | 2021 - 2022
|  |  | Sampling Frequency |  |  |  | Monthly - when discharge occurs | [14 empty] | Sampling Frequency |  |  | Monthly
|  |  | Published Date | [18 empty] | Published Date
| Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm | Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L)
|  |  | Point 1 License Conditions 100%ile | [18 empty] | Approved Concentration Limit
|  |  | 30 |  | 30 |  | 6.5-8.5 | 600 |  | 10 |  | 15 |  | 1 | N/A | 2 | [5 empty] | No limit or range defined in licence
| 2020-04-15 | 2020-04-29 | < | 5 |  | 1 | 7.26 |  | 370 | < | 5 |  | 2.7 | 0.66 | 0.54 | < | 0.5 | 64 | 68
| 2020-05-11 | 2020-05-25 | < | 5 |  | 1 | 7.14 |  | 120 | < | 5 |  | 4 | 0.24 | 0.31 | < | 0.5 | 67 | 72
| 2020-06-03 | 2020-06-18 | < | 5 | < | 1 | 6.85 |  | 90 | < | 5 |  | 5.4 | 0.05 | 0.29 | < | 0.5 | 71 | 75
| 2020-07-14 | 2020-07-30 | < | 5 | < | 1 | 6.97 |  | 77 | < | 5 |  | 4.6 | 0.09 | 0.34 | < | 0.5 | 71 | 75
| 2020-08-11 | 2020-08-24 | < | 5 | < | 1 | 7.86 |  | 110 | < | 5 |  | 8.8 | 0.24 | 0.32 | < | 0.5 | 67 | 72
| 2020-09-09 | 2020-09-24 | < | 5 |  | 1 | 7.18 |  | 7 | < | 5 |  | 6.9 | 0.17 | 0.2 | < | 0.5 | 65 | 69
| 2020-10-14 | 2020-10-27 | < | 5 |  | 2 | 7.28 |  | 10 | < | 5 |  | 3.8 | 0.36 | 0.2 | < | 0.5 | 59 | 64
| 2020-11-12 | 2020-11-24 | < | 5 |  | 3 | 7.55 |  | 61 | < | 5 |  | 3 | 1.1 | 0.28 | < | 0.5 | 56 | 60
| 2020-12-09 | 2020-12-21 | < | 5 |  | 2 | 7.16 |  | 3 | < | 5 |  | 2.7 | 1.9 | 0.2 | < | 0.5 | 51 | 56
| 2021-01-13 | 2021-01-27 | < | 5 |  | 4 | 7.26 |  | 2 | < | 5 |  | 4.9 | 1.9 | 0.22 | < | 0.5 | 56 | 62
| 2021-02-17 | 2021-03-02 | < | 5 |  | 2 | 7.04 |  | 3 | < | 5 |  | 3.6 | 0.64 | 0.22 | < | 0.5 | 57 | 62
| 2021-03-17 | 2021-03-30 | < | 5 |  | 2 | 7.06 |  | 210 | < | 5 |  | 4.9 | 0.47 | 0.2 | < | 0.5 | 60 | 64
| No of Samples Collected |  | 12 |  | 12 | 12 | 12 | 12 |  | 12 |  | 12 |  | 12 | 12 | 12 |  |  |  | No of Samples Collected |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
| Lowest Sample Value |  | < | 5 |  | 1 | 6.85 | 2 |  | < | 5 | < | 2.7 | 0.05 | 0.2 | < | 0.5 |  |  | Lowest Sample Value |  | 0 |  | 0 | 0 | 0 |  | < | 0 | < | 0 | 0 | 0 | < | 0
| Mean of Samples |  | 5 | 6.6667 | 1.75 |  | 7.2175 | 88.5833 |  | 5 | 6.6667 | 4.6083 |  | 0.65167 | 0.27667 | 0.5 |  |  |  | Mean of Samples |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
| Highest Sample Value |  | 5 |  | 4 |  | 7.86 | 370 |  | 5 |  | 8.8 |  | 1.9 | 0.54 | 0.5 |  |  |  | Highest Sample Value |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
0
[22 empty] | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799
Blayney Sewage Treatment Works - Licence Point Sampling
|  |  | License Point No. |  |  |  | 2
|  |  | Period |  |  |  | 2020 - 2021
|  |  | Sampling Frequency |  |  |  | Monthly
Published Date
Catch Pond
| Date Sample Taken | Date Reported | Biological Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm | Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm
|  |  | Approved Concentration Limit | [18 empty] | Catch Pond Summary
|  |  | No limit or range defined in licence | [16 empty] | 2019-08-14 | 2019-08-28 | 5 |  | 7 | 7.24 |  | 6700 | < | 5 |  | 9.6 | 0.19 |  | 0.7
| 2020-04-15 | 2020-04-29 | < | 5 |  | 7 | 7.9 |  | 350 | < | 5 |  | 5.6 | 0.66 | 0.7 |  | 1 | 64 | 68 | 2019-09-19 | 2019-10-01 | 5 |  | 6 | 7.28 |  | 1300 | < | 5 |  | 7.7 | 0.15 |  | 1
| 2020-05-11 | 2020-05-25 | < | 5 |  | 11 | 7.73 |  | 17 | < | 5 |  | 10 | 0.26 | 0.52 |  | 1.3 | 68 | 73 | 2019-10-17 | 2019-10-30 | 5 |  | 5 | 7.2 |  | 1400 | < | 5 |  | 9.5 | 0.24 |  | 2.1 | 64 | 68
| 2020-06-03 | 2020-06-18 | < | 5 |  | 5 | 7.51 |  | 41 | < | 5 |  | 9.2 | 0.09 | 0.41 | < | 0.5 | 73 | 77 | 2020-03-11 | 2020-03-24 | 5 |  | 4 | 7.4 |  | 2800 | < | 5 |  | 8.7 | 0.56 |  | 1.3 | 69 | 73
| 2020-07-14 | 2020-07-30 | < | 5 |  | 2 | 7.82 |  | 10 | < | 5 |  | 8.1 | 0.15 | 0.29 |  | 0.7 | 72 | 76 | 2020-04-15 | 2020-04-29 | 5 |  | 4 | 7.24 |  | 1100 | < | 5 |  | 6.6 | 0.44 |  | 1.4 | 70 | 74
| 2020-08-11 | 2020-08-24 | < | 5 | < | 1 | 7.05 |  | 34 | < | 5 |  | 7.2 | 0.22 | 0.28 | < | 0.5 | 72 | 76 | 2020-05-11 | 2020-05-25 | 5 |  | 2 | 7.36 |  | 9600 | < | 5 |  | 13 | 0.23 |  | 1.8 | 70 | 74
| 2020-09-09 | 2020-09-24 | < | 5 | < | 1 | 8.42 |  | 2 | < | 5 |  | 7.1 | 0.14 | 0.22 | < | 0.5 | 74 | 78 | 2020-06-03 | 2020-06-18 | 5 |  | 3 | 7.21 |  | 8800 | < | 5 |  | 10 | 0.09 |  | 1.4 | 73 | 77
| 2020-10-14 | 2020-10-27 | < | 5 |  | 3 | 7.94 |  | 8 | < | 5 |  | 6.4 | 0.44 | 0.22 |  | 1.3 | 67 | 71 | 2020-07-14 | 2020-07-30 | 5 |  | 7 | 7.25 |  | 410 | < | 5 |  | 11 | 0.17 |  | 1 | 69 | 73
| 2020-11-12 | 2020-11-24 | < | 5 |  | 1 | 7.99 |  | 44 | < | 5 |  | 7.2 | 1.5 | 0.23 |  | 0.7 | 62 | 66 | 2020-10-14 | 2020-10-27 | 5 |  | 6 | 7.62 |  | 23000 | < | 5 |  | 9.1 | 1.2 |  | 1.8 | 66 | 66
| 2020-12-09 | 2020-12-21 | < | 5 |  | 10 | 8.04 |  | 19 | < | 5 |  | 4.2 | 1.9 | 0.45 | < | 0.5 | 61 | 66
| 2021-01-13 | 2021-01-27 | < | 5 |  | 6 | 8.98 |  | 12 | < | 5 |  | 4.6 | 4.6 | 0.36 | < | 0.5 | 64 | 69
| 2021-02-17 | 2021-03-02 | < | 5 |  | 6 | 9.02 |  | 6 | < | 5 |  | 4.4 | 0.59 | 0.26 | < | 0.5 | 66 | 71
| 2021-03-17 | 2021-03-30 | < | 5 |  | 4 | 7.98 |  | 25 | < | 5 |  | 4.8 | 0.4 | 0.28 | < | 0.5 | 66 | 74
| No of Samples Collected |  | 12 |  | 12 | 12 | 12 | 12 |  | 12 |  | 12 |  | 12 | 12 | 12 |  | 12 | 12 | No of Samples Collected |  | 9 | 9 | 9 | 9 | 9 |  | 9 |  | 9 |  | 9 | 9 |  | 7 | 7
| Lowest Sample Value |  | < | 5 |  | 1 | 7.05 | 2 |  | < | 5 | < | 4.2 | 0.09 | 0.22 | < | 0.5 | 61 | 66 | Lowest Sample Value |  | 5 |  | 2 | 7.2 | 410 |  |  | 5 |  | 6.6 | 0.09 |  | 0.7 | 64 | 66
| Mean of Samples |  | 5 | 6.6667 | 4.75 |  | 8.0317 | 47.3333 |  | 5 | 6.6667 | 6.5667 |  | 0.9125 | 0.35167 | 0.70833 |  | 67.4167 | 72.0833 | Mean of Samples |  | 5 | 4.8889 |  | 7.3111 | 6123.3333 |  | 5 | 5 | 9.4667 |  | 0.36333 | 1.3889 |  | 68.7143 | 72.1429
| Highest Sample Value |  | 5 |  | 11 |  | 9.02 | 350 |  | 5 |  | 10 |  | 4.6 | 0.7 | 1.3 |  | 74 | 78 | Highest Sample Value |  | 5 | 7 |  | 7.62 | 23000 |  | 5 |  | 13 |  | 1.2 | 2.1 |  | 73 | 77
Flow |  | 0
Actual Load |  |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0

## 2021-2022
|  |  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799 | [7 empty] | INFRASTRUCTURE SERVICES DEPARTMENT | [8 empty] | 91 Adelaide Street BLAYNEY NSW 2799
|  |  | Blayney Sewage Treatment Works - Licence Point Sampling | [18 empty] | Blayney Sewage Treatment Works - Licence Point Sampling
|  |  | License Point No. |  |  |  | 1 | [14 empty] | License Point No. |  |  | 3
|  |  | Period |  |  |  | 2020 - 2021 | [14 empty] | Period |  |  | 2020 - 2021
|  |  | Sampling Frequency |  |  |  | Monthly - when discharge occurs | [14 empty] | Sampling Frequency |  |  | Monthly
|  |  | Published Date | [18 empty] | Published Date
| Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm | Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L)
|  |  | Point 1 License Conditions 100%ile | [18 empty] | Approved Concentration Limit
|  |  | 30 |  | 30 |  | 6.5-8.5 | 600 |  | 10 |  | 15 |  | 1 | N/A | 2 | [5 empty] | No limit or range defined in licence
| 2021-04-20 | 2021-05-04 | < | 5 |  | 1 | 7.07 |  | 7 | < | 5 |  | 3.4 | 0.14 | 1.7 | < | 0.5
| 2021-05-13 | 2021-05-14 | < | 5 |  | 1 | 6.97 |  | 62 | < | 5 |  | 3.2 | 0.28 | 0.2 | < | 0.5
| 2021-06-16 | 2021-07-01 | < | 5 |  | 1 | 6.88 |  | 6 | < | 5 |  | 2.2 | 0.54 | 0.2 | < | 0.5
| 2021-07-27 | 2021-08-06 | < | 5 |  | 1 | 7.12 |  | 4 | < | 5 |  | 3.1 | 0.14 | 0.2 |  | 2.3
| 2021-08-25 | 2021-09-10 | < | 5 |  | 21 | 7.16 |  | 1000 | < | 5 |  | 5.8 | 0.34 | 0.6 | < | 0.5
| 2021-09-16 | 2021-09-29 | < | 5 |  | 1 | 7.25 |  | 10 | < | 5 |  | 4.7 | 0.3 | 0.1 | < | 0.5
| No of Samples Collected |  | 6 |  | 6 | 6 | 6 | 6 |  | 6 |  | 6 |  | 6 | 6 | 6 |  |  |  | No of Samples Collected |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0
| Lowest Sample Value |  | < | 5 |  | 1 | 6.88 | 4 |  | < | 5 | < | 2.2 | 0.14 | 0.1 | < | 0.5 |  |  | Lowest Sample Value |  | 0 |  | 0 | 0 | 0 | < | 0 | < | 0 | 0 | 0 | < | 0
| Mean of Samples |  | 5 | 3.3333 | 4.3333 |  | 7.075 | 181.5 |  | 5 | 3.3333 | 3.7333 |  | 0.29 | 0.5 | 0.8 |  |  |  | Mean of Samples |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
| Highest Sample Value |  | 5 |  | 21 |  | 7.25 | 1000 |  | 5 |  | 5.8 |  | 0.54 | 1.7 | 2.3 |  |  |  | Highest Sample Value |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0
0
[22 empty] | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799
Blayney Sewage Treatment Works - Licence Point Sampling
|  |  | License Point No. |  |  |  | 2
|  |  | Period |  |  |  | 2020 - 2021
|  |  | Sampling Frequency |  |  |  | Monthly
Published Date
Catch Pond
| Date Sample Taken | Date Reported | Biological Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm | Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm
|  |  | Approved Concentration Limit | [18 empty] | Catch Pond Summary
No limit or range defined in licence
| 2021-04-20 | 2021-05-04 | < | 5 |  | 4 | 9.14 |  | 4 | < | 5 |  | 3.6 | 0.16 | 0.29 | < | 0.5
| 2021-05-13 | 2021-05-14 | < | 5 |  | 3 | 7.74 |  | 7 | < | 5 |  | 7.6 | 0.31 | 0.25 |  | 3
| 2021-06-16 | 2021-07-01 | < | 5 |  | 3 | 7.58 | < | 1 | < | 5 |  | 5.4 | 0.66 | 0.2 |  | 2
| 2021-07-27 | 2021-08-06 | < | 5 |  | 3 | 7.44 |  | 120 | < | 5 |  | 8.9 | 0.14 | 0.24 |  | 2.6
| 2021-08-25 | 2021-09-10 | < | 5 |  | 3 | 7.44 |  | 1300 | < | 5 |  | 8.2 | 0.36 | 0.1 |  | 3.2
| 2021-09-16 | 2021-09-29 | < | 5 |  | 1 | 9.08 |  | 1 | < | 5 |  | 5.7 | 0.35 | 0.1 | < | 0.5
| No of Samples Collected |  | 6 |  | 6 | 6 | 6 | 6 |  | 6 |  | 6 |  | 6 | 6 | 6 |  | 0 | 0 | No of Samples Collected |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 | 0
| Lowest Sample Value |  | < | 5 |  | 1 | 7.44 | 1 |  | < | 5 | < | 3.6 | 0.14 | 0.1 | < | 0.5 | 0 | 0 | Lowest Sample Value |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0
| Mean of Samples |  | 5 | 3.3333 | 2.8333 |  | 8.07 | 238.8333 |  | 5 | 3.3333 | 6.5667 |  | 0.33 | 0.19667 | 1.9667 |  | #DIV/0! | #DIV/0! | Mean of Samples |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0!
| Highest Sample Value |  | 5 |  | 4 |  | 9.14 | 1300 |  | 5 |  | 8.9 |  | 0.66 | 0.29 | 3.2 |  | 0 | 0 | Highest Sample Value |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 | 0
Flow |  | 0
Actual Load |  |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0

## 2022-2023
|  |  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799 | [7 empty] | INFRASTRUCTURE SERVICES DEPARTMENT | [9 empty] | 91 Adelaide Street BLAYNEY NSW 2799
|  |  | Blayney Sewage Treatment Works - Licence Point Sampling | [18 empty] | Blayney Sewage Treatment Works - Licence Point Sampling
|  |  | License Point No. |  |  |  | 1 |  |  | Point 1 to be sampled if discharge to river occurs | [11 empty] | License Point No. |  |  | 3
|  |  | Period |  |  |  | 2022-2023 | [14 empty] | Period |  |  | 2021-2022
|  |  | Sampling Frequency |  |  |  | If discharge to creek occurs | [14 empty] | Sampling Frequency |  |  | Monthly
|  |  | Published Date | [18 empty] | Published Date
| Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm | Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L)
|  |  | Point 1 License Conditions 100%ile | [18 empty] | Approved Concentration Limit
|  |  | 30 |  | 30 |  | 6.5-8.5 | 600 |  | 10 |  | 15 |  | 1 | N/A | 2 | [5 empty] | No limit or range defined in licence
| 2022-04-20 | 2022-05-06 | < | 5 |  | 2 | 7.05 |  | 510 | < | 5 |  | 4.9 | 0.1 | < 0.20 |  | 1.5 | 63 | 68
| 2022-05-26 | 2022-06-24 | < | 5 |  | 2 | 6.92 |  | 26 | < | 5 |  | 5.9 | 2.6 | < 0.20 | < | 0.5 | 67 | 71
| 2022-06-21 | 2022-07-08 | < | 5 |  | 1 | 7.1 | ~ | 4 | < | 5 |  | 6.9 | 0.3 | < 0.20 | < | 0.5 | 72 | 77
| 2022-07-13 | 2022-07-29 | < | 5 |  | 1 | 7.14 | ~ | 1 | < | 5 |  | 4.3 | 0.21 | < 0.20 | < | 0.5 | 74 | 78
| 2022-08-17 | 2022-08-29 | < | 5 |  | 1 | 7.18 | ~ | 2 | < | 5 |  | 4.3 | 0.26 | < 0.1 | < | 0.5 | 69 | 74
| 2022-09-07 | 2022-09-20 | < | 5 | < | 1 | 7.38 | ~ | 6 | < | 5 |  | 3.8 | 0.41 | < 0.20 | < | 0.5 | 70 | 73
| 2022-10-19 | 2022-11-02 | < | 5 |  | 3 | 7.41 | ~ | 8 | < | 5 |  | 4 | 0.23 | < 0.20 | < | 0.5 | 62 | 67
| 2022-11-21 | 2022-12-01 | < | 5 |  | 2 | 7.62 |  | 42 | < | 5 |  | 5.2 | 0.24 | 0.06 | < | 0.5 | 57 | 62
| 2022-12-07 | 2022-12-20 | < | 5 |  | 2 | 7.35 |  | 59 | < | 5 |  | 4.4 | 0.16 | < 0.20 | < | 0.5 | 64 | 69
| 2023-01-17 | 2023-01-18 | < | 5 |  | 5 | 7.08 |  | 39 | < | 5 |  | 5.8 | 0.2 | < 0.20 | < | 0.5 | 61 | 66
| 2023-02-15 | 2023-03-06 | < | 5 |  | 4 | 7.12 | ~ | 3 | < | 5 |  | 4.5 | 0.55 | 0.31 | < | 0.5 | 61 | 66
| 2023-03-22 | 2023-04-04 | < | 5 |  | 6 | 7.1 |  | 78 | < | 5 |  | 3.4 | 0.32 | 0.22 | < | 0.5 | 58 | 63
| 2023-04-12 | 2023-04-26 | < | 5 |  | 5 | 7.29 |  | 25 | < | 5 |  | 3.2 | 1.1 | < 0.20 | < | 0.5 | 64 | 69
| No of Samples Collected |  | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 |  | 13 | 12 | 13 |  | 13 | 13 | No of Samples Collected |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
| Lowest Sample Value |  | < | 5 |  | 1 | 6.92 | 1 |  | < | 5 | < | 3.2 | 0.1 | 0.06 | < | 0.5 | 57 | 62 | Lowest Sample Value |  | 0 |  | 0 | 0 | 0 |  | < | 0 | < | 0 | 0 | 0 | < | 0
| Mean of Samples |  | 5 | 7.2222 | 2.6923 |  | 7.2108 | 61.7692 |  | 5 | 7.2222 | 4.6615 |  | 0.51385 | 0.049167 | 0.57692 |  | 64.7692 | 69.4615 | Mean of Samples |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
| Highest Sample Value |  | 5 |  | 6 |  | 7.62 | 510 |  | 5 |  | 6.9 |  | 2.6 | 0.31 | 1.5 |  | 74 | 78 | Highest Sample Value |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
0
[22 empty] | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799 | [8 empty] | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799
|  |  | Blayney Sewage Treatment Works - Licence Point Sampling | [19 empty] | Blayney Sewage Treatment Works - Licence Point Sampling
|  |  | License Point No. |  |  |  | 2
|  |  | Period |  |  |  | 2022-2023 | [16 empty] | Inlet Works
|  |  | Sampling Frequency |  |  |  | Monthly
Published Date
| Date Sample Taken | Date Reported | Biological Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm |  | Date Sample Taken | Date Reported | Biological Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Total Phosphorous (mg/L)
Approved Concentration Limit
No limit or range defined in licence
| 2022-04-20 | 2022-05-06 |  | 6 |  | 10 | 7.64 |  | 700 | < | 5 |  | 3.4 | 0.5 | <0.20 | < | 0.5 | 62 | 66 |  | 2021-04-20 | 2021-05-04 |  | 231 |  | 423 | 7.64 |  | 4.6
| 2022-05-26 | 2022-06-24 | < | 5 |  | 3 | 6.85 | < | 1 | < | 5 |  | 7.2 | 3.5 | 0.21 | < | 0.5 | 69 | 73
| 2022-06-21 | 2022-07-08 | < | 5 |  | 4 | 7.33 | ~ | 1 | < | 5 |  | 9.1 | 0.36 | <0.20 |  | 2.4 | 76 | 80
| 2022-07-13 | 2022-07-29 | < | 5 |  | 2 | 7.54 | ~ | 8 | < | 5 |  | 7.3 | 0.17 | <0.20 |  | 2.4 | 74 | 78
| 2022-08-17 | 2022-08-29 | < | 5 |  | 1 | 7.46 |  | 100 | < | 5 |  | 6.2 | 0.4 | <0.1 |  | 1 | 72 | 76
| 2022-09-07 | 2022-09-20 | < | 5 |  | 2 | 7.67 | < | 1 | < | 5 |  | 6.6 | 0.58 | <0.20 |  | 1 | 73 | 76
| 2022-10-19 | 2022-11-02 | < | 5 |  | 3 | 7.68 | ~ | 2 | < | 5 |  | 6.3 | 0.28 | 0.28 |  | 1 | 73 | 77
| 2022-11-21 | 2022-12-01 | < | 5 |  | 2 | 8.02 | ~ | 2 | < | 5 |  | 5.3 | 0.23 | 0.12 | < | 0.5 | 71 | 75
| 2022-12-07 | 2022-12-20 | < | 5 |  | 2 | 9.1 | ~ | 1 | < | 5 |  | 4.5 | 0.36 | <0.20 | < | 0.5 | 72 | 76
| 2023-01-17 | 2023-01-18 | < | 5 |  | 4 | 8.64 | ~ | 3 | < | 5 |  | 4.3 | 0.22 | <0.20 | < | 0.5 | 68 | 73
| 2023-02-15 | 2023-03-06 | < | 5 |  | 1 | 7.64 |  | 24 | < | 5 |  | 4.4 | 0.32 | <0.20 | < | 0.5 | 67 | 72
| 2023-03-22 | 2023-04-04 | < | 5 |  | 14 | 8.92 |  | 41 | < | 5 |  | 3.1 | 1 | 0.32 | < | 0.5 | 62 | 67
| 2023-04-12 | 2023-04-26 | < | 5 |  | 3 | 7.75 |  | 39 | < | 5 |  | 7.2 | 1.5 | 0.22 |  | 3.5 | 67 | 71
| No of Samples Collected |  | 13 |  | 13 | 13 | 13 | 13 |  | 13 |  | 13 |  | 13 | 13 | 13 |  | 13 | 13
| Lowest Sample Value |  | < | 5 |  | 1 | 6.85 | 1 |  | < | 5 | < | 3.1 | 0.17 | 0.12 | < | 0.5 | 62 | 66
| Mean of Samples |  | 5.0769 | 7.3333 | 3.9231 |  | 7.8646 | 71 |  | 5 | 7.2222 | 5.7615 |  | 0.72462 | 0.088462 | 1.1385 |  | 69.6923 | 73.8462
| Highest Sample Value |  | 6 |  | 14 |  | 9.1 | 700 |  | 5 |  | 9.1 |  | 3.5 | 0.32 | 3.5 |  | 76 | 80
Flow |  | 0
Actual Load |  |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0

## 2023-2024
|  |  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799 | [7 empty] | INFRASTRUCTURE SERVICES DEPARTMENT | [9 empty] | 91 Adelaide Street BLAYNEY NSW 2799
|  |  | Blayney Sewage Treatment Works - Licence Point Sampling | [18 empty] | Blayney Sewage Treatment Works - Licence Point Sampling
|  |  | License Point No. |  |  |  | 1 |  |  | Point 1 to be sampled if discharge to river occurs | [11 empty] | License Point No. |  |  | 3
|  |  | Period |  |  |  | 2023-2024 | [14 empty] | Period |  |  | 2023-2024
|  |  | Sampling Frequency |  |  |  | Monthly If discharge to creek occurs | [14 empty] | Sampling Frequency |  |  | Monthly
|  |  | Published Date |  |  |  | 2024-04-30 | [14 empty] | Published Date
| Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm | Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L)
|  |  | Point 1 License Conditions 100%ile | [18 empty] | Approved Concentration Limit
|  |  | 30 |  | 30 |  | 6.5-8.5 | 600 |  | 10 |  | 15 |  | 1 | N/A | 2 | [5 empty] | No limit or range defined in licence
| 2023-04-12 | 2023-04-26 | < | 5 |  | 5 | 7.29 |  | 25 | < | 5 |  | 3.2 | 1.1 | 0.2 | < | 0.5 | 64 | 69
| 2023-05-10 | 2023-05-23 | < | 5 |  | 1 | 7.33 |  | 21 | < | 5 |  | 5.7 | 0.48 | 0.2 |  | 0.7 | 70 | 74
| 2023-06-20 | 2023-07-04 | < | 5 |  | 3 | 7.13 |  | 55 | < | 5 |  | 3.6 | 0.32 | 0.2 | < | 0.5 | 71 | 75
| 2023-07-13 | 2023-07-25 | < | 5 |  | 10 | 7.72 |  | 33 | < | 5 |  | 3.6 | 0.23 | 0.2 | < | 0.5 | 69 | 73
| 2023-08-15 | 2023-08-29 | < | 5 |  | 3 | 7.14 |  | 56 | < | 5 |  | 3.1 | 2.4 | 0.2 | < | 0.5 | 70 | 74
| 2023-09-13 | 2023-09-27 | < | 5 |  | 3 | 7.35 |  | 40 | < | 5 |  | 3.7 | 0.4 | 0.2 | < | 0.5 | 66 | 70
| 2023-10-17 | 2023-10-27 | < | 5 |  | 17 | 7.56 |  | 48 | < | 5 |  | 5.8 | 0.6 | 0.51 | < | 0.5 | 63 | 68
| 2023-11-21 | 4/11/2023* | < | 5 |  | 3 | 7.26 |  | 80 | < | 5 |  | 3.4 | 0.84 | 0.5 | < | 0.5 | 54 | 59
| 2023-12-12 | 2024-01-03 | < | 5 |  | 23 | 7.3 |  | 89 | < | 5 |  | 4 | 1.5 | 0.22 | < | 0.5 | 52 | 58
| 2024-01-16 | 2024-01-30 | < | 5 |  | 5 | 7.27 |  | 130 | < | 5 |  | 3.5 | 1.4 | 0.2 | < | 0.5 | 53 | 58
| 2024-02-21 | 2024-03-06 | < | 5 |  | 6 | 7.24 |  | 390 | < | 5 |  | 4.5 | 0.81 | 0.2 | < | 0.5 | 62 | 67
| 2024-03-13 | 2024-03-25 | < | 5 |  | 5 | 6.95 |  | 240 | < | 5 |  | 4.6 | 1.1 | 0.23 |  | 0.7 | 63 | 67
*error in date on report - assumed to be 12/4/2023
| No of Samples Collected |  | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 |  | 12 | 12 | 12 |  | 12 | 12 | No of Samples Collected |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
| Lowest Sample Value |  | < | 5 |  | 1 | 6.95 | 21 |  | < | 5 | < | 3.1 | 0.23 | 0.2 | < | 0.5 | 52 | 58 | Lowest Sample Value |  | 0 |  | 0 | 0 | 0 |  | < | 0 | < | 0 | 0 | 0 | < | 0
| Mean of Samples |  | 5 | 6.6667 | 7 |  | 7.295 | 100.5833 |  | 5 | 6.6667 | 4.0583 |  | 0.93167 | 0.255 | 0.53333 |  | 63.0833 | 67.6667 | Mean of Samples |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
| Highest Sample Value |  | 5 |  | 23 |  | 7.72 | 390 |  | 5 |  | 5.8 |  | 2.4 | 0.51 | 0.7 |  | 71 | 75 | Highest Sample Value |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
0
[22 empty] | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799 | [8 empty] | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799
|  |  | Blayney Sewage Treatment Works - Licence Point Sampling | [19 empty] | Blayney Sewage Treatment Works - Licence Point Sampling
|  |  | License Point No. |  |  |  | 2
|  |  | Period |  |  |  | 2022-2023 | [16 empty] | Inlet Works
|  |  | Sampling Frequency |  |  |  | Monthly
|  |  | Published Date |  |  |  | 2024-04-30
| Date Sample Taken | Date Reported | Biological Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm |  | Date Sample Taken | Date Reported | Biological Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Total Phosphorous (mg/L)
Approved Concentration Limit
No limit or range defined in licence
| 2023-04-10 | 2023-04-23 | < | 5 |  | 6 | 7.74 |  | 61 | < | 5 |  | 5.9 | 0.38 | 0.29 | < | 0.5 | 66 | 70
| 2023-05-10 | 2023-05-23 | < | 5 |  | 5 | 8.04 |  | 12 | < | 5 |  | 6.5 | 0.37 | 0.2 |  | 1.3 | 73 | 76
| 2023-06-20 | 2023-07-04 | < | 5 |  | 16 | 9.4 |  | 1 | < | 5 |  | 4.3 | 0.26 | 0.2 | < | 0.5 | 70 | 74
| 2023-07-13 | 2023-07-25 | < | 5 |  | 29 | 9.34 |  | 1 | < | 5 |  | 5.4 | 0.34 | 0.37 |  | 0.7 | 71 | 75
| 2023-08-15 | 2023-08-29 | < | 5 |  | 8 | 7.32 |  | 2 | < | 5 |  | 6.3 | 0.39 | 0.21 |  | 2.8 | 71 | 75
| 2023-09-13 | 2023-09-27 | < | 5 |  | 8 | 7.54 |  | 23 | < | 5 |  | 7.8 | 0.6 | 0.22 |  | 2.1 | 69 | 73
| 2023-10-17 | 2023-10-27 | < | 5 |  | 6 | 7.14 |  | 22 | < | 5 |  | 3.7 | 0.29 | 0.24 | < | 0.5 | 61 | 66
| 2023-11-21 | 4/11/2023* | < | 5 |  | 7 | 7.73 |  | 51 | < | 5 |  | 3.3 | 0.98 | 0.31 | < | 0.5 | 62 | 67
| 2023-12-12 | 2024-01-03 | < | 5 |  | 13 | 8.67 |  | 90 | < | 5 |  | 3.8 | 1.6 | 0.2 |  | 1 | 55 | 59
| 2024-01-16 | 2024-01-30 | < | 5 |  | 13 | 8.46 |  | 20 | < | 5 |  | 3.5 | 1.6 | 0.2 | < | 0.5 | 62 | 67
| 2024-02-21 | 2024-03-06 | < | 5 |  | 6 | 7.54 |  | 83 | < | 5 |  | 4.8 | 0.92 | 0.2 | < | 0.5 | 64 | 68
| 2024-03-13 | 2024-03-25 | < | 5 |  | 10 | 7.64 |  | 180 | < | 5 |  | 5.5 | 1.1 | 0.24 |  | 1.8 | 65 | 70
*error in date on report - assumed to be 12/4/2023
| No of Samples Collected |  | 12 |  | 12 | 12 | 12 | 12 |  | 12 |  | 12 |  | 12 | 12 | 12 |  | 12 | 12
| Lowest Sample Value |  | < | 5 |  | 5 | 7.14 | 1 |  | < | 5 | < | 3.3 | 0.26 | 0.2 | < | 0.5 | 55 | 59
| Mean of Samples |  | 5 | 6.6667 | 10.5833 |  | 8.0467 | 45.5 |  | 5 | 6.6667 | 5.0667 |  | 0.73583 | 0.24 | 1.0583 |  | 65.75 | 70
| Highest Sample Value |  | 5 |  | 29 |  | 9.4 | 180 |  | 5 |  | 7.8 |  | 1.6 | 0.37 | 2.8 |  | 73 | 76
Flow |  | 0
Actual Load |  |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0

## 2024-2025
|  |  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799 | [7 empty] | INFRASTRUCTURE SERVICES DEPARTMENT | [9 empty] | 91 Adelaide Street BLAYNEY NSW 2799
|  |  | Blayney Sewage Treatment Works - Licence Point Sampling | [18 empty] | Blayney Sewage Treatment Works - Licence Point Sampling
|  |  | License Point No. |  |  |  | 1 |  |  | Point 1 to be sampled if discharge to river occurs | [11 empty] | License Point No. |  |  | 3
|  |  | Period |  |  |  | 2024-2025 | [14 empty] | Period |  |  | 2024-2025
|  |  | Sampling Frequency |  |  |  | Monthly If discharge to creek occurs | [14 empty] | Sampling Frequency |  |  | Monthly
|  |  | Published Date | [18 empty] | Published Date
| Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm | Date Sample Taken | Date Reported | Biochemical Oxygen Demand (mg/L) | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L)
|  |  | Point 1 License Conditions 100%ile | [18 empty] | Approved Concentration Limit
|  |  | 30 |  | 30 |  | 6.5-8.5 | 600 |  | 10 |  | 15 |  | 1 | N/A | 2 | [5 empty] | No limit or range defined in licence
| 2024-04-10 | 2024-04-23 | < | 5 |  | 1 | 7.3 |  | 100 | < | 5 |  | 7.1 | 0.52 | 0.22 | < | 0.5 | 68 | 73
| 2024-05-14 | 2024-05-27 | < | 5 |  | 2 | 7.31 |  | 250 | < | 5 |  | 3.9 | 0.19 | 0.2 | < | 0.5 | 69 | 73
| 2024-06-19 | 2024-06-28 | < | 5 |  | 2 | 7.34 |  | 42 | < | 5 |  | 5.5 | 0.2 | 0.2 | < | 0.5 | 72 | 74
| 2024-07-30 | 2024-08-12 | < | 5 |  | 3 | 7.03 |  | 18 | < | 5 |  | 5.9 | 0.41 | 0.2 | < | 0.5 | 70 | 70
| 2024-08-15 | 2024-08-29 | < | 5 |  | 2 | 7.33 |  | 66 | < | 5 |  | 4.5 | 0.4 | 0.2 | < | 0.5 | 68 | 71
| 2024-09-18 | 2024-09-30 | < | 5 |  | 5 | 7.78 |  | 80 | < | 5 |  | 4.1 | 0.23 | 0.2 | < | 0.5 | 64 | 67
| 2024-10-16 | 2024-10-30 | < | 5 |  | 3 | 7.13 |  | 290 | < | 5 |  | 5.1 | 0.65 | 0.2 | < | 0.5 | 57 | 62
| 2024-11-19 | 2024-12-02 | < | 5 |  | 3 | 7.01 |  | 69 | < | 5 |  | 5 | 1.4 | 0.2 | < | 0.7 | 59 | 73
| 2024-12-04 | 2024-12-16 | < | 5 |  | 3 | 7.14 |  | 1300 | < | 5 |  | 5.1 | 2 | 0.2 | < | 0.5 | 66 | 72
| 2025-01-15 | 2025-01-28 | < | 5 |  | 6 | 7.28 |  | 200 | < | 5 |  | 4.8 | 1.3 | 0.2 | < | 0.5 | 68 | 71
| 2025-02-13 | 2025-02-25 | < | 5 |  | 4 | 7.1 |  | <1 | < | 5 |  | 4.4 | 1.5 | 0.21 | < | 0.5 | 65 | 70
| 2025-03-19 | 2025-03-31 | < | 5 |  | 3 | 7.14 |  | 74 | < | 5 |  | 3.8 | 1.5 | 0.2 | < | 0.5 | 60 | 66
| No of Samples Collected |  | 12 |  | 12 |  | 12 | 11 |  | 12 |  | 12 |  | 12 | 12 | 12 |  | 12 | 12 | No of Samples Collected |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
| Lowest Sample Value |  | < | 5 |  | 1 | 7.01 | 18 |  | < | 5 | < | 3.8 | 0.19 | 0.2 | < | 0.5 | 57 | 62 | Lowest Sample Value |  | 0 |  | 0 | 0 | 0 |  | < | 0 | < | 0 | 0 | 0 | < | 0
| Mean of Samples |  | 5 | 6.6667 | 3.0833 |  | 7.2408 | 226.2727 |  | 5 | 6.6667 | 4.9333 |  | 0.85833 | 0.2025 | 0.51667 |  | 65.5 | 70.1667 | Mean of Samples |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
| Highest Sample Value |  | 5 |  | 6 |  | 7.78 | 1300 |  | 5 |  | 7.1 |  | 2 | 0.22 | 0.7 |  | 72 | 74 | Highest Sample Value |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
0
[22 empty] | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799 | [8 empty] | INFRASTRUCTURE SERVICES DEPARTMENT | [10 empty] | 91 Adelaide Street BLAYNEY NSW 2799
|  |  | Blayney Sewage Treatment Works - Licence Point Sampling | [19 empty] | Blayney Sewage Treatment Works - Licence Point Sampling
|  |  | License Point No. |  |  |  | 2
|  |  | Period |  |  |  | 2024-2025 | [16 empty] | Inlet Works
|  |  | Sampling Frequency |  |  |  | Monthly
Published Date
| Date Sample Taken | Date Reported | Biological Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Faecal Coliforms (units/100 mL) |  | Oil & Grease (mg/L) |  | Total Nitrogen (mg/L) |  | Total Phosphorous (mg/L) | Aluminium (mg/L) | Ammonia - N (mg/L) |  | UVT % @ 254nm | UVT % @ 270nm |  | Date Sample Taken | Date Reported | Biological Oxygen Demand (mg/L) |  | Total Suspended Solids (mg/L) |  | pH | Total Phosphorous (mg/L)
Approved Concentration Limit
No limit or range defined in licence
| 2024-04-10 | 2024-04-23 | < | 5 |  | 6 | 7.74 |  | 61 | < | 5 |  | 5.9 | 0.38 | 0.29 |  | 3.5 | 66 | 70
| 2024-05-14 | 2024-05-27 | < | 5 |  | 3 | 7.65 |  | 58 | < | 5 |  | 4.4 | 0.24 | 0.2 |  | 2.1 | 70 | 75
| 2024-06-19 | 2024-06-28 | < | 5 |  | 3 | 7.62 |  | 60 | < | 5 |  | 7.8 | 0.33 | 0.2 |  | 2.4 | 71 | 73
| 2024-07-30 | 2024-08-12 | < | 5 |  | 12 | 8.38 |  | 57 | < | 5 |  | 6.6 | 0.5 | 0.2 |  | 0.7 | 75 | 74
| 2024-08-15 | 2024-08-29 | < | 5 |  | 14 | 9.52 |  | <1 | < | 5 |  | 5 | 0.42 | 0.2 | < | 0.5 | 72 | 75
| 2024-09-18 | 2024-09-30 | < | 5 |  | 5 | 7.54 |  | 9 | < | 5 |  | 3.8 | 0.43 | 0.32 |  | 1.3 | 61 | 64
| 2024-10-16 | 2024-10-30 | < | 5 |  | 3 | 8.4 |  | 16 | < | 5 |  | 5.5 | 0.87 | 0.31 |  | 1 | 61 | 66
| 2024-11-19 | 2024-12-02 | < | 5 |  | 8 | 7.56 |  | 300 | < | 5 |  | 6.5 | 1.5 | 0.32 |  | 1.5 | 64 | 78
| 2024-12-04 | 2024-12-16 | < | 5 |  | 6 | 7.62 |  | 57 | < | 5 |  | 4.5 | 2 | 0.2 |  | 1.6 | 63 | 69
| 2025-01-15 | 2025-01-28 | < | 5 |  | 9 | 8.77 |  | 180 | < | 5 |  | 4.5 | 1 | 0.2 | < | 0.5 | 76 | 78
| 2025-02-13 | 2025-02-15 | < | 5 |  | 10 | 7.75 |  | <1 | < | 5 |  | 6.5 | 1.9 | 0.22 |  | 2.7 | 52 | 58
| 2025-03-19 | 2025-03-31 | < | 5 |  | 17 | 7.82 |  | 500 | < | 5 |  | 3.9 | 0.98 | 0.2 |  | 1 | 52 | 58
| No of Samples Collected |  | 12 |  | 12 | 12 | 12 | 10 |  | 12 |  | 12 |  | 12 | 12 | 12 |  | 12 | 12
| Lowest Sample Value |  | < | 5 |  | 3 | 7.54 | 9 |  | < | 5 | < | 3.8 | 0.24 | 0.2 | < | 0.5 | 52 | 58
| Mean of Samples |  | 5 | 6.6667 | 8 |  | 8.0308 | 129.8 |  | 5 | 6.6667 | 5.4083 |  | 0.87917 | 0.23833 | 1.5667 |  | 65.25 | 69.8333
| Highest Sample Value |  | 5 |  | 17 |  | 9.52 | 500 |  | 5 |  | 7.8 |  | 2 | 0.32 | 3.5 |  | 76 | 78
Flow |  | 0
Actual Load |  |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0